## Equipment List
Project | Step | Equipment Type | Equipment Type | Material | Purpose | Capacity / L | Equipment No. |  | Tank Check | [5 empty] | Valve Check |  |  |  | Cleaning Check |  |  |  | Tank Nozzle Piping Connection Check |  |  |  | Polishing Check |  |  |  | Lighting Check |  |  |  |  | Agitator Check |  |  |  | Tee Dead-Leg Check |  |  |  | Instrument Check
[8 empty] | Category | Tank | Compliant? (Description) | P&ID before Retrofit | Non-compliance Photo | P&ID after Retrofit | Retrofit Photo | Valves (diaphragm valve installation angle) | Compliant? (Description) | Non-compliance Photo | Retrofit Photo | Cleaning | Compliant? (Description) | Non-compliance Photo | Retrofit Photo | Tank Nozzle Piping Connection | Compliant? (Description) | Non-compliance Photo | Retrofit Photo | Polishing | Compliant? (Description) | Non-compliance Photo | Retrofit Photo | Lighting | Compliant? (Description) | Non-compliance Photo | Retrofit Photo | Humidified Nitrogen | Agitator | Compliant? (Description) | Non-compliance Photo | Retrofit Photo | Dead Legs at Tees | Compliant? (Description) | Non-compliance Photo | Retrofit Photo | Location | Instrument Compliance | Compliant? (Description) | P&ID before Retrofit | Non-compliance Photo | P&ID after Retrofit | Retrofit Photo | Documentation | Risk Assessment
139788 | step3 | TFF | Tank | 316L | Hold Tank | 1000L | TJ4S-1211-TFF02-T01 | Category 4 | 316L | Non-compliant Replace the tank with a BPE-compliant tank; Separate inlet for each material; Add in-line CIP to the tank; |  |  |  | To be provided after retrofit | Diaphragm valve | No, level gauge diaphragm valve angle non-compliant, prone to product hold-up; |  | To be provided after retrofit | Removable for cleaning, drainable, compliant | Compliant | N/A | N/A | Clamp connections on site, compliant | Compliant | N/A | N/A | Compliant Internal surface finish: NMT 25 µin Ra or 0.63 µm | Compliant | N/A | N/A | Sight-glass light provided | Non-compliant, no sight-glass light |  | To be provided after retrofit |  | Not applicable | N/A | N/A | N/A | 3D compliant, minimum dead-leg design | No, tee on the water inlet line is too long, cleaning dead leg present |  | To be provided after retrofit | LT-001 differential-pressure level transmitter | No, manual valve installed on the side port of the DP level transmitter | Root connection at tank does not meet 3D |  |  |  | To be provided after retrofit | Compliant
[16 empty] | No, level gauge diaphragm valve angle non-compliant, prone to product hold-up; | [27 empty] | PT-001 remote-reading pressure gauge | No, manual valve installed below the pressure gauge | Root connection at tank does not meet 3D |  |  |  | To be provided after retrofit | Compliant
[16 empty] | No, pneumatic diaphragm valve angle on the feed line non-compliant, prone to product hold-up; other valve angles acceptable | [24 empty] | No, tee lengths at tank bottom outlet and drain port non-compliant, cleaning dead legs present; |  | To be provided after retrofit | TT-001 temperature sensor | No, thermometer is of the dip-tube type | BPE does not allow dip-tube thermometers |  |  |  | To be provided after retrofit | Compliant
Root connection at tank does not meet 2D
|  |  | TFF | 316L | TFF | 30m2 | TJ4S-1211-TFF02 | Category 4 | 316L | Compliant |  | N/A | N/A | N/A | Diaphragm valve | Compliant | N/A | N/A | Removable for cleaning, drainable, compliant | Compliant Ball valve downstream of the check valve on the waste drain line; all others are diaphragm valves | N/A | N/A | Clamp connections on site, compliant | Compliant | N/A | N/A | Compliant Internal surface finish: NMT 25 µin Ra or 0.63 µm | Compliant | N/A | N/A | Sight-glass light provided | Compliant, sight-glass light provided | N/A | N/A |  | Tank has a bottom-mounted agitator | N/A | N/A | N/A | 3D compliant, minimum dead-leg design | Compliant | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Compliant

## Piping List
Project | Step | Process Step | Line From | Line To | Material / Size | Fluid | Piping Standard | Connection Check |  |  |  | Piping Standard |  |  |  | Valve Type Check |  |  |  | Cleaning Check |  |  |  | Polishing Check |  |  |  | Slope Check |  |  |  | Non-drainable Flowmeter Check |  |  |  | Low-Point Drain Check
[8 empty] | Connection Type | Compliant? (Description) | Non-compliance Photo | Retrofit Photo | Piping Standard | Compliant? (Description) | Non-compliance Photo | Retrofit Photo | Valve Type | Compliant? (Description) | Non-compliance Photo | Retrofit Photo | Cleaning | Compliant? (Description) | Non-compliance Photo | Retrofit Photo | Polishing | Compliant? (Description) | Non-compliance Photo | Retrofit Photo | Slope | Compliant? (Description) | Non-compliance Photo | Retrofit Photo | Non-drainable Flowmeter | Compliant? (Description) | Non-compliance Photo | Retrofit Photo | Low-point drain on line? | Compliant? (Description) | Non-compliance Photo | Retrofit Photo | Documentation | Risk Assessment
139788 | step3 | TFF | TJ4S-1211-HPPC03-AT03 | TJ4S-1211-TFF02-T01 | 316L Stainless Steel/DN25 | Prep fraction addition | Category 4 | Sanitary clamp | Compliant | N/A | N/A | BPE | Compliant | N/A | N/A | Diaphragm valve | Compliant | N/A | N/A | 1. Line can be CIP-cleaned, with forward and reverse flushing; 2. 3D design to minimize residual dead legs; | Non-compliant |  | To be provided after retrofit | Compliant | Compliant | N/A | N/A | Slope > 1%, fully drainable | Compliant | N/A | N/A | Flowmeter installed vertically | Compliant | N/A | N/A | Line low points meet 3D; | Non-compliant |  | To be provided after retrofit | Compliant
|  |  | TJ4S-1211-TFF02-T01 | TJ4S-1211-TFF02 | 316L Stainless Steel/DN25 | Prep fraction and methanol addition | Category 4 | Sanitary clamp | Compliant | N/A | N/A | BPE | Compliant | N/A | N/A | Diaphragm valve | Compliant | N/A | N/A | 1. Line is CIP-capable; 2. Line filter cleaned offline; filter replaced by a jumper for CIP; 3. Line filter body: add a drain point; 4. 3D design to minimize residual dead legs; | Non-compliant |  | To be provided after retrofit | Compliant | Compliant | N/A | N/A | Slope > 1%, fully drainable | Compliant | N/A | N/A | Not applicable | Not applicable | N/A | N/A | No low-point drain | Non-compliant No low-point drain on line No low-point drain on filter |  | To be provided after retrofit | Compliant
|  |  | Solvent Drum | TJ4S-1211-TFF02 | 316L Stainless Steel/DN25 | ACN / water addition | Category 3 | Sanitary clamp | Compliant | N/A | N/A | BPE | Non-compliant; line to be replaced with BPE tubing; | N/A | To be provided after retrofit | Diaphragm valve | Compliant | N/A | N/A | 1. Solvent line purged with N2, no in-line CIP; 2. Line filter cleaned offline; 3. 3D design to minimize residual dead legs; | Non-compliant |  | To be provided after retrofit | Compliant | Compliant | N/A | N/A | Slope > 1%, fully drainable | Compliant | N/A | N/A | Not applicable | Not applicable | N/A | N/A | 1. Add a line low point for gravity drainage; 2. Line filter body: add a drain point; | Pneumatic pump: drains before/after pump, N2 purge; ACN filter inlet has a drain port | No low-point drain | To be provided after retrofit | Compliant
|  |  | CNC-Solvent | TJ4S-1211-TFF02-T01 | 316L Stainless Steel/DN25 | Methanol addition | Category 3 | Sanitary clamp | Compliant | N/A | N/A | BPE | Non-compliant; line to be replaced with BPE tubing; | N/A | To be provided after retrofit | Diaphragm valve | Compliant | N/A | N/A | 1. Solvent line purged with N2, no in-line CIP; 2. Line filter cleaned offline; 3. Drummed solvent can be fed directly to the equipment or via a spray ball; 4. 3D design to minimize residual dead legs; | Non-compliant |  | To be provided after retrofit | Compliant | Compliant | N/A | N/A | Slope > 1%, fully drainable | Compliant | N/A | N/A | Not applicable | Not applicable | N/A | N/A | 1. Add a line low point for gravity drainage; 2. Line filter body: add a drain point; | Pneumatic pump: drains before/after pump, N2 purge; |  | To be provided after retrofit | Compliant
|  |  | TJ4S-1211-R02 | TJ4S-1211-TFF02 | 316L Stainless Steel/DN25 | NaOH solution addition | Category 3 | Sanitary clamp | Compliant | N/A | N/A | BPE | Non-compliant; line to be replaced with BPE tubing; | N/A | To be provided after retrofit | Diaphragm valve | Compliant | N/A | N/A | 1. Line is CIP-capable; 3. Line filter cleaned offline; filter replaced by a jumper for CIP; 6. 3D design to minimize residual dead legs; | Non-compliant |  | To be provided after retrofit | Compliant | Compliant | N/A | N/A | Slope > 1%, fully drainable | Compliant | N/A | N/A | Not applicable | Not applicable | N/A | N/A | 1. Add a line low point for gravity drainage; 2. Line filter body: add a drain point; | No low-point drain Non-compliant | No low-point drain | To be provided after retrofit | Compliant

## 09.02.26 Meeting (2) (hidden)
BLA Topic: 09.02.2026 Questions - Ciara |  | Responses
Priority 1 | 1. Humidifier Design a. Please provide detail of WFI addition (from loop to humidifier- full process): in what container? How is it transported to building 12? How is it connected? How long can you hold the wfi and do you have hold studies or planned studies? What controls will be in place to ensure at time of use this meets WFI quality. If a vessel is used for transporting WFI, is there pressure control/monitoring to ensure this remains positive to the environment? b. Needs to take action to change flanges as this should be cat 4 and needs to be in grade C (if hose connections).- is this feasible? When? c. If no hoses and hard piped, then: i. Filter between humidifier and AFD must be in grade C ii. 1st filter for nitrogen can reside with the humidifier in CNC | ## Short-term (before WFI is available in BLD#12): The humidifier will be located in the CNC area and transferred to the AFD via fixed piping and filters. Rationale: Since the WFI system is not yet available, locating the humidified‑nitrogen system in Grade C would require WFI transfer into the Grade C area. In addition, periodic water replacement for humidified‑nitrogen would introduce extra operations and risks in Grade C area. Based on risk comparison, short‑term placement in the CNC area is adopted to minimize operations inside Grade C. Associated risks can be effectively controlled via defined risk‑control strategies. Control Measures: WFI‑filling procedure: (BLD#4) 1. The WFI drum (316L Stanless Steel) shall be pre‑depyrogenated (caustic cleaning followed by water rinsing). Filters for nitrogen supply and vent shall be fitted to the WFI drum. 2. Prior to water charging, the connected hoses and drum shall be rinsed with WFI, and the rinse WFI shall be drained completely. 3. Charge WFI into the drum. Upon completion of charging, maintain slight positive nitrogen pressure protection. Blind flanges shall be fitted on all piping connections. Transfer the drum in closed condition to BLD#12 Humidified‑nitrogen feeding procedure: (BLD#12) 1. The humidifier water tank shall be equipped with a spray ball. Filters shall be installed on the charging port, nitrogen inlet and vent port. 2. Prior to use, the charging piping, tank and pump shall be treated with caustic solution and rinsed with purified water to acceptance criteria. 3. Check the nitrogen pressure of the transferred WFI drum. If pressure is abnormal, repeat the water‑filling and transfer procedure. If pressure is normal, connect the pump and transfer piping. Rinse the humidifier tank with WFI circulated through the piping and pump. 4. After completion of WFI rinsing, close the bottom nozzle, and charge the required volume of WFI into the tank. 5. The generated humidified nitrogen shall pass through a 0.22 filter inside Grade C before entering the AFD. ## Long‑term Measures (after WFI is available in BLD#12 approx by JAN27) Locate the humidifier within Grade C area. CIP function shall be added after delivery of the nitrogen humidifier. Control Measures: 1. Connect the WFI point‑of‑use to the humidifier water tank via hose. Perform caustic cleaning and water rinsing by CIP for depyrogenation. 2. The water inside the humidifier tank shall be replaced periodically. The humidifier shall be disinfected before standby‑for‑use.
| 2. For R05, AT01, AT02 (and their associated transfer lines) - should be cat 4 since growth promoting- address asap, prefer before saleable batches. - what is feasible from Asymchem side? | R05, AT01, AT02 are concentrated‑salt preparation & hold tanks; solutions are growth‑promoting per Lilly assessment. Existing equipment fails Category 4 (C4) due to tank flanges, plunger pump flanges etc. Enhanced cleaning & disinfection is planned for microbial risk reduction. T01 (purified‑water hold) tank with tri‑clamp diaphragm valves and NA connections meet C4. Nitrogen‑vent tri‑clamp ball valve only meets C3 compliance. (plan to change it to tri-clam diaphragm valve to meet C4) Plunger pump has flange connections. Cleaning‑disinfection strategy: Disinfection before every batch to lower microbial bioburden. Main equipment: caustic disinfection. Flange joints (tank, pump, control valve): disassembled, cleaned, verified and disinfected. Pump chambers & control‑valve cavities (non‑dis‑mountable): caustic flushing after full piping assembly. Piping: caustic flushing after full assembly. Disinfection procedure: 1. Charge caustic into R05; run preparation sequence across R05‑AT01‑AT02 (T01 is also caustic treated) up to Mobile Phase A/B tanks. 2. Purified‑water flush via preparation sequence until neutral pH. 3. ACN flush; vent ACN from tanks; piping preserved in ACN for bacteriostatic effect. 4. Displace full preparation system with process fluid via preparation sequence before use. Long‑term options: 1. Option1: Upgrade full preparation system including R05 to C4‑compliant in‑line preparation system. 2. Option2: Direct batch preparation of ACN‑containing mobile phase. Final Category 3 / Category 4 requirement depends on Lilly evaluation whether GG917 mobile phase is growth‑promoting / non‑growth‑promoting. Concentrated‑salt tanks and associated lines shall meet C4 due to required one‑time preparation. Procurement for both options to start ASAP; timeline to be jointly assessed with engineering, procurement and vendor.
3. T01 same as above - tank appears it meets cat 4- can you confirm? (in list you assess to cat.3). Transfer line is non-compliant. What is feasible? T02-T03
| 4. Can you confirm redispensing of crude prior to disso will be performed in a ISO 8/grade D equivalent environment? - was previously stated and want to confirm. | Yes, crude prior to disso will be performed in a ISO 8/grade D environment.
| 5. For raw material dispensing (e.g. NH4Ac salt, tris base solid, resin for chrom column) in what environment will these be dispensed- can you provide general setup details here? (expectation would be same environment as crude redispense ISO8/grade D) | Raw material will also be dispensed in ISO8/grade D area. Using glove box (see an example on the right)
| 6. LHM does not meet cat.4 - where will the justification/risk assessment be captured? (i.e. ball valves and non triclamp fittings present). | HPPC, HPLC, ball valve type confirmation. P&ID show flange, need justification.
| 7. AFD- Can you confirm if threaded fittings used inside AFD or not? Something we have seen before on: antisolvent wash bars, agitator bellows hubs, gas knife nozzles, dust filter element, cleaning rings | There is threaded fitting used for agitator bellows hub. - see pics on the right-hand side need justification to acknowledge it. Bottom bellow high risk.
| 8. Growth promoting solution vessels: what controls are in place? e.g. Time limits for use of the solution? a. Similarly- Static mixer: for transfer lines that remain liquid full - what is the controls around this liquid? ACN solution vs. NaOH (or make sure NaOH gets removed completed) as cleaning angent? | 1. For growth‑promoting‑solution vessels R05, AT01, AT02, T01 and associated transfer lines: equipment train shall be disinfected with 1 M NaOH before production. Vessels: spray‑ball / recirculated spray rinse. Transfer lines: flushing via solution‑preparation process sequence. Post‑disinfection purified‑water rinse per SOP to neutral pH; equipment train then ready for production. 2. Inter‑batch cleaning for the equipment train: R05, AT01, AT02 disassembled for cleaning; T01 spray‑ball‑rinsed with purified water; transfer lines purified‑water‑flushed via preparation sequence. Follow‑up acetonitrile flushing for lines; vessel acetonitrile vented and N₂‑blown‑dry. Piping preserved in acetonitrile for bacteriostatic effect. 3. Before subsequent batch: displace equipment‑train piping with mobile phase via preparation sequence. 4. Asymchem will perform laboratory studies to assess hold‑time of growth‑promoting salt solutions.
| 9. Solid additions- for salts what is the process here? Same as crude addition? (containment valves? Open addition?) | Solid additions will be the same as crude addition, furthermore, we will replace bufferfly valve with split bufferfly valve to ensure contained charging.
| 10. Purified water hoses- can you outline all steps where these are used and what controls are planned? | TBD
Priority 2 | 1. Filter list- Can we get a list of filter type, micron and location
2. Technical review excel- we have responses here we will add- once added I can inform you- this can be continued offline/ in the next session.