<Power Supply Changeover Test Record>

《供电线路切换测试记录》

| Operation Category 操作类别 | Mains dual-circuit line switching市电双回路线路切换□ Generator line switching发电机线路切换□ |  |  |
| --- | --- | --- | --- |
| Test Department 测试部门 |  |  |  |
| Operator操作人 |  | Start time开始时间 |  |
| Involves power supply circuit information涉及供电回路信息 |  |  |  |
| Transformer number of the line to be switched待切换线路变压器编号 |  | Municipal Power Line Number所属市电线路编号 |  |
| Transformer number of the line to be connected待并入线路变压器编号 |  | Municipal Power Line Number所属市电线路编号 |  |
| Enable Generator Number启用发电机编号 |  |  |  |
| Operating steps操作步骤 |  |  |  |
| Operating position操作位置 | Operating Requirements操作要求 |  | After completion, the operator shall sign to confirm.完成后操作人签字确认 |
| Subject to the main cabinet number受总柜编号 | Press the trip button; once the trip indicator light illuminates, withdraw the locked disconnect switch to the open position, lock it, remove the key, and hang up a “Power Off” sign.按下分闸按钮，分闸指示灯亮起后，摇出带锁隔离开关至分闸位上锁并拔出钥匙悬挂停电标牌。 |  |  |
| Double-circuit interconnection cabinet number双回路联络柜编号 | Rotate the lockable isolating switch to the closed position, insert the key to release the lock, and press the closing button; the closing indicator light will illuminate.摇入带锁隔离开关至合闸位，插入钥匙解除锁定，按下合闸按钮，合闸指示灯亮起。 |  |  |
| Generator Interconnection Cabinet Number发电机联络柜编号 | Rotate the isolating switch to the closed position, press the manual closing button, and the closing indicator light will illuminate.摇入隔离开关至合闸位，按下手动合闸按钮，合闸指示灯亮起。 |  |  |
| Confirm after switching lines切换线路完成后确认 |  |  |  |
| Confirm Project确认项目 | Achievement criteria达成标准 |  | Reviewer’s Signature复核人签字 |
| Operation Time操作用时 | Complete the circuit switching operation within 30 minutes and record the completion time. 30分钟内完成线路切换操作，并记录完成时间： |  |  |
| Supply Voltage供电电压 | After completing the line switching operation, verify that the voltage of the target energized circuit is normal and record the measured value.线路切换操作完成后目标送电回路电压是否正常，并记录数值 Uab: Ubc: Uac: |  |  |