## Equipment List
项目 | 步骤 | 设备类型 | 设备类型 | 材质 | 用途 | 容量/ L | 设备编号 |  | 储罐排查项 | [5 empty] | 阀门排查项 |  |  |  | 清洁排查项 |  |  |  | 罐口管路连接方式排查项 |  |  |  | 抛光排查项 |  |  |  | 照明排查项 |  |  |  |  | 搅拌桨排查项 |  |  |  | 三通死角排查项 |  |  |  | 仪表排查项
[8 empty] | 等级 | 储罐 | 是否符合，并描述 | 改造前PID图纸 | 不符合照片 | 改造后PID图纸 | 改造照片 | 阀门（隔膜阀是否有角度） | 是否符合，并描述 | 不符合照片 | 改造照片 | 清洁 | 是否符合，并描述 | 不符合照片 | 改造照片 | 罐口管路连接方式 | 是否符合，并描述 | 不符合照片 | 改造照片 | 抛光 | 是否符合，并描述 | 不符合照片 | 改造照片 | 照明 | 是否符合，并描述 | 不符合照片 | 改造照片 | 湿氮气 | 搅拌桨 | 是否符合，并描述 | 不符合照片 | 改造照片 | 三通处造成的死角 | 是否符合，并描述 | 不符合照片 | 改造照片 | 位置 | 仪表是否符合要求 | 是否符合，并描述 | 改造前PID图纸 | 不符合照片 | 改造后PID图纸 | 改造照片 | 文件资料 | 风险评估
139788 | step3 | 超滤 | Tank | 316L | 暂存罐 | 1000L | TJ4S-1211-TFF02-T01 | Category 4 | 316L | 不符合 需要将储罐更换为满足BPE需求储罐; 物料单独进; 储罐增加在线CIP清洗; |  |  |  | 待改造后提供 | 隔膜阀 | 否，液位计隔膜阀角度不符合，易存料； |  | 待改造后提供 | 可拆卸清洗，可排空，合规 | 符合要求 | N/A | N/A | 现场为卡箍连接，符合要求 | 符合要求 | N/A | N/A | 符合要求 内表面粗糙度：NMT 25Ra（微英寸）或 0.63 微米 | 符合要求 | N/A | N/A | 有视镜灯 | 不符，无视镜灯 |  | 待改造后提供 |  | 不涉及 | N/A | N/A | N/A | 符合3D，最小死角设计 | 否，进水管路三通过长，存在清洁死角 |  | 待改造后提供 | LT-001差压液位计 | 否，差压液位计侧口安装手阀 | 储罐根部不满足3D需求 |  |  |  | 待改造后提供 | Compliant
[16 empty] | 否，液位计隔膜阀角度不符合，易存料； | [27 empty] | PT-001远传压力表 | 否，压力表下口安装手阀 | 储罐根部不满足3D需求 |  |  |  | 待改造后提供 | Compliant
[16 empty] | 否，进料管线气动隔膜阀角度不符合要求，易存料；其余阀门角度合格 | [24 empty] | 否，罐底出料和排液口三通长度不符合，存在清洁死角； |  | 待改造后提供 | TT-001温度计 | 否，温度计为内伸管 | BPE不允许内伸温度计 |  |  |  | 待改造后提供 | Compliant
储罐根部不满足2D需求
|  |  | TFF | 316L | 超滤 | 30m2 | TJ4S-1211-TFF02 | Category 4 | 316L | 符合要求 |  | N/A | N/A | N/A | 隔膜阀 | 符合要求 | N/A | N/A | 可拆卸清洗，可排空，合规 | 符合要求 废液排放管路的止逆阀后端使用球阀，其他为隔膜阀 | N/A | N/A | 现场为卡箍连接，符合要求 | 符合要求 | N/A | N/A | 符合要求 内表面粗糙度：NMT 25Ra（微英寸）或 0.63 微米 | 符合要求 | N/A | N/A | 有视镜灯 | 符合，有视镜灯 | N/A | N/A |  | 储罐有下搅拌 | N/A | N/A | N/A | 符合3D，最小死角设计 | 符合要求 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Compliant

## Piping List
项目 | 步骤 | 工序 | 管路起始 | 管路结束 | 材质/管径 | 液相 | 管路标准 | 连接方式排查项 |  |  |  | 管路标准 |  |  |  | 阀门类型排查项 |  |  |  | 清洁排查项 |  |  |  | 抛光排查项 |  |  |  | 坡度排查项 |  |  |  | 不可排尽流量计排查项 |  |  |  | 低点排尽排查项
[8 empty] | 连接方式 | 是否符合，并描述 | 不符合照片 | 改造照片 | 管路标准 | 是否符合，并描述 | 不符合照片 | 改造照片 | 阀门类型 | 是否符合，并描述 | 不符合照片 | 改造照片 | 清洁 | 是否符合，并描述 | 不符合照片 | 改造照片 | 抛光 | 是否符合，并描述 | 不符合照片 | 改造照片 | 坡度 | 是否符合，并描述 | 不符合照片 | 改造照片 | 不可排尽的流量计 | 是否符合，并描述 | 不符合照片 | 改造照片 | 管路是否有低点排尽口 | 是否符合，并描述 | 不符合照片 | 改造照片 | 文件 | 风险评估
139788 | step3 | 超滤 | TJ4S-1211-HPPC03-AT03 | TJ4S-1211-TFF02-T01 | 316L Stainless Steel/DN25 | 制备组分加入 | Category 4 | 卫生卡箍 | 符合要求 | N/A | N/A | BPE | 符合要求 | N/A | N/A | 隔膜阀 | 符合要求 | N/A | N/A | 1.管路可进行CIP清洗.可正洗、反洗； 2.使用３D减少残留死区； | 不符合 |  | 待改造后提供 | 符合要求 | 符合要求 | N/A | N/A | 坡度大于1%，实现完全排空 | 符合要求 | N/A | N/A | 流量计竖直安装 | 符合 | N/A | N/A | 管路低点满足3D需求； | 不符合 |  | 待改造后提供 | 符合要求
|  |  | TJ4S-1211-TFF02-T01 | TJ4S-1211-TFF02 | 316L Stainless Steel/DN25 | 制备组分及甲醇溶剂加入 | Category 4 | 卫生卡箍 | 符合要求 | N/A | N/A | BPE | 符合要求 | N/A | N/A | 隔膜阀 | 符合要求 | N/A | N/A | 1.管路可实现CIP； 2.管路过滤器-离线清洗，过滤器短接进行CIP清洗； 3.管道过滤器本体：增加排净点； 4.使用３D减少残留死区； | 不符合 |  | 待改造后提供 | 符合要求 | 符合要求 | N/A | N/A | 坡度大于1%，实现完全排空 | 符合要求 | N/A | N/A | 不涉及 | 不涉及 | N/A | N/A | 无低点排尽口 | 不符合 管路无低点排净 过滤器无低点排净 |  | 待改造后提供 | 符合要求
|  |  | Solvent Drum | TJ4S-1211-TFF02 | 316L Stainless Steel/DN25 | 乙腈/水加入 | Category 3 | 卫生卡箍 | 符合要求 | N/A | N/A | BPE | 不符合要求，管路需更换为BPE管路； | N/A | 待改造后提供 | 隔膜阀 | 符合要求 | N/A | N/A | 1.溶剂管路通过N2进行吹扫，不进行在线CIP； 2.管路过滤器-离线清洗； 3.使用３D减少残留死区； | 不符合 |  | 待改造后提供 | 符合要求 | 符合要求 | N/A | N/A | 坡度大于1%，实现完全排空 | 符合要求 | N/A | N/A | 不涉及 | 不涉及 | N/A | N/A | 1.增加管路低点可实现重力排净点； 2.管道过滤器本体：增加排净点； | 气动泵：泵前及泵后有排净，氮气吹扫； 乙腈过滤器进口带排净口 | 无低点排净 | 待改造后提供 | 符合要求
|  |  | CNC-Solvent | TJ4S-1211-TFF02-T01 | 316L Stainless Steel/DN25 | 甲醇加入 | Category 3 | 卫生卡箍 | 符合要求 | N/A | N/A | BPE | 不符合要求，管路需更换为BPE管路； | N/A | 待改造后提供 | 隔膜阀 | 符合要求 | N/A | N/A | 1.溶剂管路通过N2进行吹扫，不进行在线CIP； 2.管路过滤器-离线清洗； 3.桶装溶剂可直接进设备或通过喷淋球进设备; 4.使用３D减少残留死区； | 不符合 |  | 待改造后提供 | 符合要求 | 符合要求 | N/A | N/A | 坡度大于1%，实现完全排空 | 符合要求 | N/A | N/A | 不涉及 | 不涉及 | N/A | N/A | 1.增加管路低点可实现重力排净点； 2.管道过滤器本体：增加排净点； | 气动泵：泵前及泵后有排净，氮气吹扫； |  | 待改造后提供 | 符合要求
|  |  | TJ4S-1211-R02 | TJ4S-1211-TFF02 | 316L Stainless Steel/DN25 | 氢氧化钠溶液加入 | Category 3 | 卫生卡箍 | 符合要求 | N/A | N/A | BPE | 不符合要求，管路需更换为BPE管路； | N/A | 待改造后提供 | 隔膜阀 | 符合要求 | N/A | N/A | 1.管路可实现CIP； 3.管路过滤器-离线清洗，过滤器短接进行CIP清洗； 6.使用３D减少残留死区； | 不符合 |  | 待改造后提供 | 符合要求 | 符合要求 | N/A | N/A | 坡度大于1%，实现完全排空 | 符合要求 | N/A | N/A | 不涉及 | 不涉及 | N/A | N/A | 1.增加管路低点可实现重力排净点； 2.管道过滤器本体：增加排净点； | 无低点排净 不符合 | 无低点排净 | 待改造后提供 | 符合要求

## 09.02.26 Meeting (2) (hidden)
BLA Topic：09.02.2026 Questions - Ciara |  | Responses
Priority 1 | 1. Humidifier Design a. Please provide detail of WFI addition (from loop to humidifier- full process): in what container? How is it transported to building 12? How is it connected? How long can you hold the wfi and do you have hold studies or planned studies? What controls will be in place to ensure at time of use this meets WFI quality. If a vessel is used for transporting WFI, is there pressure control/monitoring to ensure this remains positive to the environment? b. Needs to take action to change flanges as this should be cat 4 and needs to be in grade C (if hose connections).- is this feasible? When? c. If no hoses and hard piped, then: i. Filter between humidifier and AFD must be in grade C ii. 1st filter for nitrogen can reside with the humidifier in CNC 1. 加湿器设计 a. 请提供注射用水 WFI 加入的完整详情（从循环管网至加湿器的完整工艺流程）：WFI 接收至什么容器？如何输送至 12 号厂房？采用何种连接方式？WFI 可储存多长时间？是否已开展储存时限研究或计划开展该研究？将采取哪些控制手段，确保使用时刻 WFI 质量符合要求。 若采用容器转运 WFI：是否设置压力控制 / 压力监测，保证容器相对环境始终维持正压？ b. 需要采取措施更改法兰，该部分应属于 Category4，若采用软管连接则需布置在 C 级洁净区。该方案是否可行？何时完成？ c. 如果不使用软管，采用硬管连接，则： i. 加湿器与 AFD 之间的过滤器必须布置在 C 级洁净区； ii. 氮气的第一道过滤器可随加湿器布置在 CNC（受控非分级）区域。 | ## Short-term (before WFI is available in BLD#12): The humidifier will be located in the CNC area and transferred to the AFD via fixed piping and filters. Rationale: Since the WFI system is not yet available, locating the humidified‑nitrogen system in Grade C would require WFI transfer into the Grade C area. In addition, periodic water replacement for humidified‑nitrogen would introduce extra operations and risks in Grade C area. Based on risk comparison, short‑term placement in the CNC area is adopted to minimize operations inside Grade C. Associated risks can be effectively controlled via defined risk‑control strategies. Control Measures: WFI‑filling procedure: (BLD#4) 1. The WFI drum (316L Stanless Steel) shall be pre‑depyrogenated (caustic cleaning followed by water rinsing). Filters for nitrogen supply and vent shall be fitted to the WFI drum. 2. Prior to water charging, the connected hoses and drum shall be rinsed with WFI, and the rinse WFI shall be drained completely. 3. Charge WFI into the drum. Upon completion of charging, maintain slight positive nitrogen pressure protection. Blind flanges shall be fitted on all piping connections. Transfer the drum in closed condition to BLD#12 Humidified‑nitrogen feeding procedure: (BLD#12) 1. The humidifier water tank shall be equipped with a spray ball. Filters shall be installed on the charging port, nitrogen inlet and vent port. 2. Prior to use, the charging piping, tank and pump shall be treated with caustic solution and rinsed with purified water to acceptance criteria. 3. Check the nitrogen pressure of the transferred WFI drum. If pressure is abnormal, repeat the water‑filling and transfer procedure. If pressure is normal, connect the pump and transfer piping. Rinse the humidifier tank with WFI circulated through the piping and pump. 4. After completion of WFI rinsing, close the bottom nozzle, and charge the required volume of WFI into the tank. 5. The generated humidified nitrogen shall pass through a 0.22 filter inside Grade C before entering the AFD. ## Long‑term Measures (after WFI is available in BLD#12 approx by JAN27) Locate the humidifier within Grade C area. CIP function shall be added after delivery of the nitrogen humidifier. Control Measures: 1. Connect the WFI point‑of‑use to the humidifier water tank via hose. Perform caustic cleaning and water rinsing by CIP for depyrogenation. 2. The water inside the humidifier tank shall be replaced periodically. The humidifier shall be disinfected before standby‑for‑use.
| 2. For R05, AT01, AT02 (and their associated transfer lines) - should be cat 4 since growth promoting- address asap, prefer before saleable batches. - what is feasible from Asymchem side? 2. 针对 R05、AT01、AT02 设备及其配套转移管线：因介质具有促微生物生长特性，应划分为 Category4，请尽快落实整改，优先在商业化合格批次生产前完成。凯莱英方面可实现的方案是什么？ | R05, AT01, AT02 are concentrated‑salt preparation & hold tanks; solutions are growth‑promoting per Lilly assessment. Existing equipment fails Category 4 (C4) due to tank flanges, plunger pump flanges etc. Enhanced cleaning & disinfection is planned for microbial risk reduction. T01 (purified‑water hold) tank with tri‑clamp diaphragm valves and NA connections meet C4. Nitrogen‑vent tri‑clamp ball valve only meets C3 compliance. (plan to change it to tri-clam diaphragm valve to meet C4) Plunger pump has flange connections. Cleaning‑disinfection strategy: Disinfection before every batch to lower microbial bioburden. Main equipment: caustic disinfection. Flange joints (tank, pump, control valve): disassembled, cleaned, verified and disinfected. Pump chambers & control‑valve cavities (non‑dis‑mountable): caustic flushing after full piping assembly. Piping: caustic flushing after full assembly. Disinfection procedure: 1. Charge caustic into R05; run preparation sequence across R05‑AT01‑AT02 (T01 is also caustic treated) up to Mobile Phase A/B tanks. 2. Purified‑water flush via preparation sequence until neutral pH. 3. ACN flush; vent ACN from tanks; piping preserved in ACN for bacteriostatic effect. 4. Displace full preparation system with process fluid via preparation sequence before use. Long‑term options: 1. Option1: Upgrade full preparation system including R05 to C4‑compliant in‑line preparation system. 2. Option2: Direct batch preparation of ACN‑containing mobile phase. Final Category 3 / Category 4 requirement depends on Lilly evaluation whether GG917 mobile phase is growth‑promoting / non‑growth‑promoting. Concentrated‑salt tanks and associated lines shall meet C4 due to required one‑time preparation. Procurement for both options to start ASAP; timeline to be jointly assessed with engineering, procurement and vendor.
3. T01 same as above - tank appears it meets cat 4- can you confirm? (in list you assess to cat.3). Transfer line is non-compliant. What is feasible? 3. T01 同上：该储罐看起来满足 Category4 要求，能否予以确认？（清单中评估为 Category3）。其转移管线不满足要求，贵方可实现的整改方案是什么？ T02-T03
| 4. Can you confirm redispensing of crude prior to disso will be performed in a ISO 8/grade D equivalent environment? - was previously stated and want to confirm. 4. 请确认粗品在溶解前的重新分装操作，是否在 ISO8/D 级等效环境内进行？该点之前已有说明，现需要再次确认。 | Yes, crude prior to disso will be performed in a ISO 8/grade D environment.
| 5. For raw material dispensing (e.g. NH4Ac salt, tris base solid, resin for chrom column) in what environment will these be dispensed- can you provide general setup details here? (expectation would be same environment as crude redispense ISO8/grade D) 5. 关于原辅料分装（例如醋酸铵盐、三羟甲基氨基甲烷固体、色谱柱用树脂），以上物料将在什么环境下进行分装？能否提供大体配置细节？（我方期望与粗品重新分装环境一致，即 ISO8/D 级） | Raw material will also be dispensed in ISO8/grade D area. Using glove box (see an example on the right)
| 6. LHM does not meet cat.4 - where will the justification/risk assessment be captured? (i.e. ball valves and non triclamp fittings present). 6. LHM 设备不满足 Category4 要求；相关论证 / 风险评估文件将归集在何处？（设备存在球阀以及非快开卡箍接头） | HPPC, HPLC, ball valve type confirmation. P&ID show flange, need justification.
| 7. AFD- Can you confirm if threaded fittings used inside AFD or not? Something we have seen before on: antisolvent wash bars, agitator bellows hubs, gas knife nozzles, dust filter element, cleaning rings 7. AFD 三合一设备：请确认 AFD 设备内部是否使用螺纹接头。我方过往项目中，以下位置曾出现螺纹接头：反溶剂冲洗杆、搅拌器波纹管轮毂、气体刀喷嘴、粉尘过滤元件、清洗环 | There is threaded fitting used for agitator bellows hub. - see pics on the right-hand side need justification to acknowledge it. Bottom bellow high risk.
| 8. Growth promoting solution vessels: what controls are in place? e.g. Time limits for use of the solution? a. Similarly- Static mixer: for transfer lines that remain liquid full - what is the controls around this liquid? 8. 促微生物生长溶液的储罐：设置了哪些控制措施？例如溶液使用的时间时限？ a. 同理，静态混合器：对于始终充满液体的转移管线，针对管内液体设置了哪些管控措施？ ACN solution vs. NaOH (or make sure NaOH gets removed completed) as cleaning angent? | 1. For growth‑promoting‑solution vessels R05, AT01, AT02, T01 and associated transfer lines: equipment train shall be disinfected with 1 M NaOH before production. Vessels: spray‑ball / recirculated spray rinse. Transfer lines: flushing via solution‑preparation process sequence. Post‑disinfection purified‑water rinse per SOP to neutral pH; equipment train then ready for production. 2. Inter‑batch cleaning for the equipment train: R05, AT01, AT02 disassembled for cleaning; T01 spray‑ball‑rinsed with purified water; transfer lines purified‑water‑flushed via preparation sequence. Follow‑up acetonitrile flushing for lines; vessel acetonitrile vented and N₂‑blown‑dry. Piping preserved in acetonitrile for bacteriostatic effect. 3. Before subsequent batch: displace equipment‑train piping with mobile phase via preparation sequence. 4. Asymchem will perform laboratory studies to assess hold‑time of growth‑promoting salt solutions.
| 9. Solid additions- for salts what is the process here? Same as crude addition? (containment valves? Open addition?) 9. 固体投料：盐类物料的投料工艺是怎样的？是否与粗品投料工艺一致？（使用密闭阀？敞口投料？） | Solid additions will be the same as crude addition, furthermore, we will replace bufferfly valve with split bufferfly valve to ensure contained charging.
| 10. Purified water hoses- can you outline all steps where these are used and what controls are planned? 10. 纯化水软管：请列出纯化水软管所有使用工序节点，以及计划采取的各项控制措施。 | TBD
Priority 2 | 1. Filter list- Can we get a list of filter type, micron and location 1. 过滤器清单：请提供过滤器清单，包含过滤器类型、精度（μm）以及安装位置。
2. Technical review excel- we have responses here we will add- once added I can inform you- this can be continued offline/ in the next session. 2. 技术评审 Excel 表格：我方会把评审意见补充进表格；补充完成后会通知贵方；该部分可线下继续沟通，或放到下一次会议讨论。