Executive Summary for Lead Team

The meeting focused on a subset of high-risk site readiness items that could impact pre-PPQ timelines, with particular emphasis on cleaning strategy, equipment/piping readiness, solvent header integrity, contamination-control measures, and purified water system risks. Overall, the Lilly team stated that most actions appear to be progressing appropriately, but several items remain potential gating activities for pre-PPQ start and require additional evidence, documentation, or mitigation plans. Lilly Site Visit Action Tracker Follow Up

1. Cleaning Strategy & Equipment Readiness (SPPS / Cleavage)

Decision

The team agreed that the immediate pre-PPQ concern is not completion of all future cleaning SOP improvements, but rather demonstrating that equipment entering pre-PPQ has been appropriately cleaned and is in a qualified state.

Key Alignment

- Existing cleaning execution records from demo activities need to be reviewed by Lilly.

- Future enhancements to cleaning SOPs and records can continue in parallel and are not required to be fully finalized prior to pre-PPQ.

- Confidence in equipment condition entering pre-PPQ is the immediate requirement.

Assigned Actions

| Action | Owner | Deliverable |
| --- | --- | --- |
| Share executed cleaning records and evidence of cleaning performed after demo activities, particularly SPPS equipment | Yan / ECM Team | Cleaning records and summary of completed cleaning activities |
| Provide updated cleaning SOP and cleaning record package for Lilly review | Yan | Revised cleaning documentation |
| Schedule follow-up discussion after Lilly reviews documentation | ECM + Lilly SMEs | Risk assessment of equipment readiness |

Risk Assessment

High Risk because readiness of SPPS equipment and cleanliness state may affect pre-PPQ authorization.

2. Cleaning Documentation for Hard-to-Clean Components / Piping Gaps

Decision

The team agreed that any cleaning challenges created by equipment design or piping configuration must be explicitly captured in cleaning documentation.

Key Alignment

Where spray coverage, nozzle geometry, dead legs, or inaccessible surfaces exist:

- Components must be specifically identified.

- Cleaning records must demonstrate how effectiveness will be assured.

- Manual cleaning activities must be traceable.

Assigned Actions

| Action | Owner | Deliverable |
| --- | --- | --- |
| Update cleaning SOPs and records to identify all critical components requiring special cleaning | Yan / ECM Team | Enhanced SOPs and records |
| Define cleaning approach for components that cannot be adequately cleaned through automated means | ECM Team | Cleaning strategy in controlled documents |

Risk Assessment

Linked directly to acceptance of known equipment design gaps.

3. Line Sloping & Piping Modification Strategy

Decision

Purification-system sloping concerns must be resolved before purification pre-PPQ activities.

Key Alignment

Discussion clarified that:

- The original action item was narrowly focused on suspected improper line slopes observed during the site visit.

- Broader piping modification efforts are occurring simultaneously.

- Purification piping slope corrections are expected before pre-PPQ.

- SPPS/Cleavage systems require risk assessment for potential drainage and dead-leg concerns.

Assigned Actions

| Action | Owner | Deliverable |
| --- | --- | --- |
| Clarify piping modification plan and completion dates | Alex / ECM Team | Updated schedule |
| Share scope of all planned piping modifications | Alex / ECM Team | Modification list |
| Identify which deficiencies will remain at pre-PPQ start and define mitigation strategy | ECM Team | Gap assessment and cleaning controls |

Risk Assessment

Moderate to High Risk Particularly if modifications remain incomplete entering pre-PPQ.

Leadership Watch Item

Any unresolved piping deficiencies must become documented accepted risks supported by cleaning controls.

4. Raw Material Staging (CNC Area) / Contamination-Control Risk

Decision

Long-term facility upgrades may take substantial time, therefore a short-term risk mitigation approach is required before pre-PPQ.

Key Alignment

The currently identified contamination-control concern will likely remain in place through pre-PPQ.

Lilly requested:

- Administrative controls

- Procedural controls

- Operator practices

- Pest and physical contamination mitigation measures

These controls must supplement the longer-term facility modifications.

Assigned Actions

| Action | Owner | Deliverable |
| --- | --- | --- |
| Develop short-term contamination-control strategy | Alex / ECM Team | Mitigation plan |
| Incorporate risk and controls into CCS documentation | ECM Team | CCS updates |
| Evaluate procedural controls and operational safeguards | ECM Team | Risk reduction measures |

Risk Assessment

High Risk Control strategy must be defined before pre-PPQ operation.

5. Solvent Header Passivation, Weld Quality & Metals Risk

Most Significant Risk Discussed

Decision

This was identified as one of the highest-risk topics discussed.

Lilly expressed concern regarding:

- Observed rust/residue event

- Weld quality concerns

- Solvent header condition

- Potential metal impurity contribution to process risks

The team agreed:

- Tank passivation and header passivation are separate issues.

- Weld integrity concerns must be evaluated independently.

- Additional inspections are likely required before pre-PPQ.

Key Leadership Message

Lilly clearly indicated that:

Confidence is required that solvent distribution systems and welds are not introducing metals into the process.

The discussion emphasized that filtration alone is unlikely to satisfy quality concerns.

Assigned Actions

Immediate

| Action | Owner | Deliverable |
| --- | --- | --- |
| Share photographs of observed rusted weld | Yu / ECM Team | Visual evidence |
| Determine weld type (manual vs orbital) | ECM Team | Technical assessment |
| Assess whether other similar welds exist | ECM Team | Scope determination |
| Provide solvent header drawings and identify common vs unique piping sections | ECM Team | Engineering package |

Short-Term Strategy

| Action | Owner | Deliverable |
| --- | --- | --- |
| Evaluate spot-checking, borescoping, or visual inspection of similar welds | ECM Team | Inspection strategy |
| Reassess passivation timeline if limited only to solvent headers | Yan / Engineering Team | Updated schedule |
| Develop proposal for pre-PPQ risk mitigation | ECM Team | Risk reduction plan |

Gating Concern

The Lilly team repeatedly indicated this issue could become a pre-PPQ gating activity if insufficient evidence is provided regarding:

- Weld integrity

- Metals risk

- Solvent header condition

- Deviation closure support

Leadership Watch Item

This is likely the top technical readiness risk coming out of the meeting.

6. Purified Water Header & Water-for-Cleaning Risk

Decision

The team acknowledged that similar purified-water-system design risks may exist outside purification operations and must be evaluated across all process steps.

Key Alignment

For SPPS and cleavage:

- Water is used for cleaning activities.

- Stagnation and unverified water quality remain potential concerns.

- Immediate modifications may not be feasible.

Therefore:

Short-term controls + risk assessments + long-term remediation strategy are required.

Assigned Actions

| Action | Owner | Deliverable |
| --- | --- | --- |
| Develop short-term and long-term purified-water risk strategy | Yan / ECM Team | Risk mitigation plan |
| Assess all water-use points across process steps | ECM Team | System review |
| Provide risk assessment supporting operation prior to full remediation | ECM Team | Risk assessment package |

Risk Assessment

Moderate to High Risk Likely manageable through documented risk acceptance and controls but needs formal justification.

Lead Team Prioritized Action List

Highest Priority / Potential Pre-PPQ Gating Items

- Solvent header passivation, weld quality investigation, and metals risk assessment

  - Pictures

  - Weld inspections

  - Header assessment

  - Revised timeline

- Demonstration of adequate cleaning status for SPPS equipment entering pre-PPQ

  - Cleaning records

  - Evidence of cleaning execution

- Raw material staging contamination-control mitigations

  - Immediate administrative controls

  - CCS updates

- Purified-water risk strategy

  - Short-term controls

  - Risk assessments

Secondary Priority

- Purification piping slope verification and modification tracking

- Enhanced cleaning SOP and cleaning record development