## Action Tracker
Number | Category | Action Item | Implementation Timing | Implementation Effort | Proposed target completion date | Existing approach | Action Plan | Questions | Lilly Response | Scope | Status | Notes | Asymchem Lead Owner | Lilly QA
1 | BLA/technical | Cleaning validation and verification strategy needs presented. Including: strategy for determining appropriate cleaning solution and conditions (time, temp etc), how these are tranlasted to the operational record to ensure proper execution in a repeatable manner. Additionaly need to share how small parts and manual cleaned components are managed and integrated into cleaning records. Additionally, how are rinse and swab limits, sampling instructions, and results recorded. | Prior to Pre-PPQ | High > 1 month | Manual Cleaning Procedure step1: 10/07/2026 step2: 10/20/2026 step3A: 11/09/2026 step3B: 11/28/2026 | -- | The cleaning validation and verification strategy was discussed with the customer on September 25, 2026. Dedicated cleaning SOPs and master batch cleaning records will be prepared for each step prior to Pre-PPQ. An example will be provided to customer for review ASAP. | -- | Need to align on cleaning interval length for each step which will establish frequency of "major" cleaning. When an interval is applied, what is the strategy for hold duration between batches within an interval? When will the cleaning master batch record be required for SPPS? After first batch? This may drive the timeline and ugency for alignement on cleaning strategy and documentation. Until this is developed what instructions will Asymchem use to complete appropriate cleaning between Step 3 demo and PPQ start to ensure the equipment is sufficiently clean? What cleaning record was executed after Step 1/Step 2 Demo - can we review this? Please ensure that cleaning SOPs/records are inclusive of any product contact misc. component cleaning required (filter housings, pumps, etc.) that may not be readily cleaned by CIP cycle. Also, for each step, please point us to where rinse/swab limit calculations exist so we can review these. Additionally, please specify how many cleaning verification vs. validation runs will be executed and when cleaning validation will be started (with respect to PPQ) for each step. | All Steps | Open | The team feels we need to have confidence that Asymchem can adequately clean equipment prior making saleable GMP material | Production / Yanlong Li 生产/李延龙 | QA / Weijiang Liu QA/刘维江
2 | Technical | Install or verify nameplate on rupture disk | Prior to Demo | Low < 1 week | 2026-09-27 | -- | Please refer to the slides ( link in Column L) | -- |  | Purification | Completed | Asymchem_Visit_Action_Tracker_Partial Feedback_09-29-2026.pptx | Production / Yanlong Li 生产/李延龙 | N/A
3 | Technical | Confirm inlet line sizing meets the 200 L/h process requirement | Prior to Demo | Low < 1 week | 2026-09-30 | -- | Theoretical calculation by IEPE; on-site testing. Please refer to the slides ( link in Column L) | -- | AJM: Acceptable. Consider point closed. | Purification | Open | Asymchem_Visit_Action_Tracker_Partial Feedback_09-29-2026.pptx | Production / Linchong Liu 生产/刘林冲 | N/A
4 | BLA | During field walkthroughs several lines visual appeard slopped in undesired location. Confirm all lines are sloped (including flexible hoses) to appropriate low points with proper drain point. | Prior to Pre-PPQ | Med > 1 week < 1 Month | Option 1: No CIP. Equipment connections meet 2D requirement; transfer piping section does not meet 3D requirement. Disassembly cleaning will be required afterwards. Completion date: 12/17/2026 Option 2: No CIP. Equipment connections meet 2D requirement with CIP ports reserved. Most of the transfer piping meets 2D requirement and minimum 3D requirement. Completion date: 01/20/2027 Option 3: In-line CIP. The vessel and piping are designed entirely following the 2D design philosophy. Completion date: 04/25/2027 | Modification and installation of the C3 and C4 lines are complete, and slope verification is in progress. The C1 and C2 lines were previously assessed as having no slope requirement, and only drain points were provided; the slope requirement needs to be re-discussed and confirmed. | Assess and inspect each process step and each line individually. | The requirement for the C1 and C2 lines is drainability, with no specific slope requirement. How should the slope be confirmed? | Need further discussion to clarify Asymchem's proposed options. Not sure we are following what the Options in column F mean. | All Steps | Open |  | Engineering / Hongjie Guo Production / Junfeng Zhang 工程/郭宏杰 生产/张俊峰 | QA / Meijia Liu QA/刘美佳
5 | Technical | Missing sight-glass lights | Post PPQ | Med > 1 week < 1 Month | 2026-12-30 | The entire equipment train is being reviewed; any missing sight-glass lights will be procured. | An inspection checklist is being established. | -- | Please ensure insructions are provided in MOR to use flashlights as needed to complete visual inspections inside tanks in the interim. | All Steps | Open | Interim measure recommended to use flashlights through sight glasses to perform visual inspections | Engineering / Hongjie Guo 工程/郭宏杰 | N/A
6 | Technical | Review HCl charging dip-tube arrangement and confirm material of construction | Prior to Demo | Low < 1 week | 2026-10-03 | -- | Provide the material-of-construction certificate and adjust(shorten) the current dip-tube length. | -- | AJM: Sounds good. For diptube, if adding above surface, make sure that flow is directed into liquid heel of tank and not towards any surfaces. If using sub-surface, ensure that you can prevent non-homogenity concerns in line. For material, if using PTFE, consider impacts of permeation - consider PFA as alternative. | Purification | Open | Source note suggests HC; confirm exact alloy/specification | IEPE / Mingzhi Zheng Production / Xingtao Fan IEPE/郑明智 生产/范兴涛 | QA / Qi Wang QA/王琪
7 | Technical | Update MOR or SOP to require mobile-scale reading after the peristaltic pump empties the flexible connection | Prior to Demo | Low < 1 week | 2026-10-03 | -- | Update the MOR to include the detailed requirement. | -- | AJM: No additional follow up needed if consifrmed in MOR. Just want to ensure enough detail is present to ensure that we accurately account for what made it into the tank. | Purification | Open | Follow up with Peter to clarify this item | Production / Yanlong Li 生产/李延龙 | QA / Qi Wang QA/王琪
8 | Technical | Observed waste header from process without check valves. Assess process piping connections for back flow risk and install check valves as necessary | Prior to Pre-PPQ | Med > 1 week < 1 Month | 2026-11-03 | -- | To be carried out together with the overall piping construction for step 3 | -- | Please evaluate steps 1 and 2 rigs to confirm if similar gaps exist | All Steps | Open |  | Production / Yanlong Li 生产/李延龙 | N/A
9 | BLA | CNC raw material staging area lacks appropriate controls. Evaluate options and implement short term safeguards to reduce risk associated with the lack of a CNC material-flow buffer zone and differential-pressure interlock in Workshop 12 CNC | Prior to Pre-PPQ | Med > 1 week < 1 Month | 2026-10-20 | -- | Submit the change control document to carry out renovation on the factory logistics passage. An airlock will be added before raw materials are transferred into the CNC area. | -- | Need to propose and implement short term administrative controls to address this gap until the long term facility modificaition can be made | All Steps | Open |  | Engineering / Hongjie Guo Production / Hui Ma 工程/郭宏杰 生产/马辉 | QA / Meijia Liu QA/刘美佳
10 | Technical | Justify the one-month service life for dedicated PW hoses | Post PPQ | Low < 1 week | 2026-12-30 | One-month service life for dedicated PW hoses. | Perform a use/disinfection-period study on dedicated PW hoses and redefine their lifecycle. | -- |  | All Steps | Open | Is 1 month replacement too conservative? Could lifetime be extended? What was basis for 1 month replacement frequency? | Production / Chunpeng Hu 生产/胡春鹏 | QA / Xiong Xiong QA/熊熊
11 | BLA/technical | Review lifecycle management for dedicated product contact and solvent hoses. Recommend visual inspection of hoses with some frequency regardless of campaign length. | Prior to Pre-PPQ | Low < 1 week | step1: 10/07/2026 step2: 10/20/2026 step3A: 11/09/2026 step3B: 11/28/2026 | -- | Revise the SOP to define the corresponding requirements. | -- | No additional follow up required. However, please ensure spare hoses are on order/in hand for critical hoses in the event a replacement is needed. | All Steps | Open |  | Production / Kai Liu 生产/刘凯 | QA / Xiong Xiong QA/熊熊
12 | BLA/technical | Review pre-use cleaning for solvent transfer and process-solution transfer hoses. Current practice to rinse new product contact hoses with methanol followed by water and dry with nitrogen after 1st installation. Recommend using process solvent in place of water and methanol. | Prior to Demo | Med > 1 week < 1 Month | 2026-10-05 | -- | Hoses have completed cleaning. A solvent run is planned prior to Step3 Demo production. After completion of the solvent run, the hoses will be cleaned with process solvent. | -- | Update procdure to ensure future new hose installations are rinsed with solvent prior to use (Not water/methanol as last fuild through the hose prior to use in the process) | All Steps | Open | Prevent contamination of demo batch that could impact representativeness. | Production / Yanlong Li Linchong Liu 生产/李延龙 刘林冲 | QA / Weijiang Liu QA/刘维江
13 | BLA | Curently site uses corrugated hoses for process and solvent transers. Upgrade to smooth-bore internal design, considering Pharmaline N hoses. | Prior to Pre-PPQ | Med > 1 week < 1 Month | 2026-11-30 | Platinum-cured silicone hoses are used. | Replacement is planned. | -- | Intent is to replace with smooth bore hoses prior to PPQ start for each step. If not possible please specify where corrugated will be used in the short term. Please clarify the MOC of process/solvent contacting hoses. Are they silicone? We were under the impression they were PTFE and only water hoses were silicone. | All Steps | Open | Effort is dependent on lead time for new hoses | Production / Yanlong Li 生产/李延龙 | QA / Zhiqiang Sun QA/孙志强
14 | Impurity Investigation | Review supplier options for reliable sourcing of DIPEA containing less than 50 ppm acetaldehyde | Prior to Pre-PPQ | Med > 1 week < 1 Month | Discuss separately | -- | -- | -- |  | SPPS | Open |  | Project Team / Xinyi Zhu 项目组/朱新义 | N/A
15 | Impurity Investigation | Complete evaluation of internal DIPEA processing options to further reduce acetaldehyde content | Prior to Pre-PPQ | Med > 1 week < 1 Month | Discuss separately | -- | -- | -- |  | SPPS | Open |  | Project Team / Xinyi Zhu 项目组/朱新义 | N/A
16 | Impurity Investigation | Evaluate options to reduce DIPEA exposure time during washing steps (such as larger DIPEA containers and/or addition of a larger dedicated makeup tank) | Prior to Pre-PPQ | Low < 1 week | Discuss separately | -- | -- | -- |  | SPPS | Open |  | Project Team / Xinyi Zhu 项目组/朱新义 | N/A
17 | Impurity Investigation | Evaluate feasability to increase nitrogen sparge rates for SC coupling to reduce HCN concentration. Confirm equipment limitations and establish the qualified operating envelope for higher nitrogen sparging rates | Prior to Pre-PPQ | Low < 1 week | Discuss separately | -- | -- | -- |  | SPPS | Open | Current equipment reportedly supports up to ~40 m³/h; current operating limit ~20 m³/h | Project Team / Xinyi Zhu 项目组/朱新义 | N/A
18 | Impurity Investigation | Assess feasibility and effectiveness of nitrogen sweep operation during SC coupling to reduce HCN concentration. | Prior to Pre-PPQ | Low < 1 week | Discuss separately | -- | -- | -- |  | SPPS | Open |  | Project Team / Xinyi Zhu 项目组/朱新义 | N/A
19 | Impurity Investigation | Complete planned passivation of GG917 and LAARA process lines. Confirm there are not similar gaps on cleavage and purification process lines for GG917 steps. | Prior to Pre-PPQ | Low < 1 week | L1 Step 1 Completed; Step 2: 10/06/2026 L2 Step 1 Completed; Step 2: 10/06/2026 L3 Step 1 Completed; Step 2: 10/06/2026; Step 3: 10/08/2026 GG917 Step 1 Completed; Step 2: 10/05/2026; Step 3: Completed | No passivation on the inner surface of process lines. | Perform passivation of GG917 and LAARA process lines. | -- | No additional follow up needed on approach. However, please clarify the difference between the two "Step 3"'s provided in column F. | All Steps | Open |  | Production / Zhongyao Zhang, Fan Wang 生产/张忠尧、王帆 | QA / Mingyang Yang QA/杨明旸
20 | Impurity Investigation | Provide a remediation plan and timeline for passivation of all bulk solvent tanks and headers | Prior to Pre-PPQ | High > 1 month | 2027-02-17 | The Phase I tank farm will not be passivated for now; metal-ion testing is performed instead. | After the Phase II tank farm is handed over, its lines and tanks will be passivated, and all subsequent projects will use solvents from the Phase II tank farm. | -- | Further discussion needed on strategy to address concerns with unpassivated solvent header tanks, piping, and weld quality based on obsvervations from recent deviation. How long would it take to passivate solvent headers and/or inspect a subset of welds for rust via visual inspection or boroscope? Was the weld involved in the residue investigation a hand weld? | All Steps | Open |  | Tank Farm / Wenyi Zhang 罐区/张文艺 | QA / Meijia Liu QA/刘美佳
21 | Impurity Investigation | Implement administrative controls for raw material receipt and transfer into CNC areas to minimize potential exposure to outdoor conditions. | Prior to Pre-PPQ | Med > 1 week < 1 Month | 2026-10-20 | There is an administrative requirement that, once material arrives at the production workshop, a dedicated operator must transfer it to the CNC area. | Update the SOP to include detailed material lifecycle management to avoid gaps during material transfer. | -- | To be clear, our expectation would be that there should be specific recording of time received at the outdoor dock and time moved into building by Operations. This will provide traceability with respect to how long material was exposed to outdoor conditions. Time outdoors should be minimized. | All Steps | Open |  | Production / Hui Ma 生产/马辉 | QA / Zhiqiang Sun QA/孙志强
22 | BLA | Define long-term facility modifications to provide an airlock or physical segregation for transer of raw materials into CNC area for stagging. | Post PPQ | High > 1 month | 2026-10-20 | -- | Submit the change control document to carry out renovation on the factory logistics passage. An airlock will be added before raw materials are transferred into the CNC area. | -- | No additional follow up. | All Steps | Open |  | Engineering / Hongjie Guo Production / TBD 工程/郭宏杰 生产/ | QA / Meijia Liu QA/刘美佳
23 | BLA | Complete review of the site multiproduct cross-contamination risk assessment and incorporate high level summary of risk and mitigations into the process specific CCS docments for each process steps | Prior to Pre-PPQ | Med > 1 week < 1 Month | 2026-10-20 | The CCS document lacks a detailed description. | Add a detailed description to the CCS document. | -- | JOB: Lilly will review CCS and provide feedback | All Steps | Open |  | QA / Qi Wang QA/王琪
24 | Technical | Replace silicone water hoses with PTFE hoses or provide a documented technical justification | Post PPQ | Med > 1 week < 1 Month | 2026-11-30 | Silicone water hoses are currently used. | Replace silicone hoses with PTFE hoses. | -- | No additional follow up. | Purification | Open | Silicone could pose risk to process if shedding occurs as PTFE is inherient and more inert | Production / Chunpeng Hu 生产/胡春鹏 | QA / Xiong Xiong QA/熊熊
25 | BLA | Update procedure to ensure immediate water hose disconnection and controlled storage after use | Prior to Demo | Med > 1 week < 1 Month | 10/04/2026 | No clear time requirement in the SOP for disconnecting water hoses after use. | Update the SOP to require that water hoses be disconnected immediately once water charging is finished. | -- | AJM: Additionally, please confirm that when water hose connections are made that draining of the hose after use is considered to prevent water from getting on equipment/floor during disconnection. | Purification | Open | Prevent biofilm formation during Demo processing that could impact PPQ. | Production / Kai Liu 生产/刘凯 | QA / Xiong Xiong QA/熊熊
26 | BLA | Update CCS for each process step to clearly define the filtration strategy in alignment with the corporate filtration gudiance. Include filtration location, type, replacement criteria, justification and diagrams or tables to CCS documentation for each process step | Prior to Pre-PPQ | Med > 1 week < 1 Month | 2026-10-11 | The detailed filtration principle is not included in CCS document. | Update CCS document to include the detailed filtration principle. | -- | AJM: Please provide an example of what this will look like at your earliest convinence for feedback from the Lilly team. In the example, please include a variety of filter types (particualte control only, bioburden control, raw material/utility, etc.), so we can provide meaningful feedback. | All Steps | Open |  | Project Team / Xinyi Zhu 项目组/朱新义 | QA / Shenghui Yu QA/于生辉
27 | BLA | Filtration of liquid raw materials is required for all process steps. Reassess and document justification for 75-micron filtration of SPPS raw material drum charging. | Prior to Demo | Med > 1 week < 1 Month | 2026-10-04 | No aglined requirement for liquid material filtration. | Update MOR to 10-micron. | -- | AJM: Please confirm that this applies to all raw material charges throughout the process (Step 1, 2, 3A/3B). 10 micron is more reasonable but still not consistent with guidance that you shared for other particualte control filters (0.45 micron per your other guidance). On site we had discussed using something like the Parker ZCTP1-045C-N-PP Fluroplus filter - is there a reason you elected to go away from this? | All Steps | Open | Prevent particulate contamination of equipment which may impact PPQ (particualte can be challenging to remove once introduced). | Production / Fan Wang 生产/王帆 | QA / Shenghui Yu QA/于生辉
28 | BLA | Revise glovebox cleaning practices to use approved alcohol wipes rather than water wipes in dispensing areas. | Prior to Demo | Low < 1 week | 2026-10-04 | Water is used for glovebox cleaning. | After water cleaning, an IPA wipe shall be performed to avoid any water residue. | -- | AJM: No additional concern. JOB: Do we have solubility data to support water and IPA wipes removing potential residual material? Or, is visually clean the only control? | All Steps | Open |  | Production / Kai Liu 生产/刘凯 | QA / Zhiqiang Sun QA/孙志强
29 | BLA | Complete planned upgrades and demonstrate CNC area relative humidity remains below 60% during summer conditions | Post PPQ | High > 1 month | 2027-05-30 | The current humidity control capability of the air conditioning system meets requirements. As winter is approaching, the outdoor ambient temperature and humidity will be low, and the existing system can satisfy humidity control requirements. Modification is planned to be completed before the arrival of high-temperature and high-humidity conditions in summer 2027, to ensure that the system can still meet the humidity control specifications after modification under summer operating conditions. | Modify the air handling units by adding cooling coils, and complete qualification during a production gap. | -- | No additional follow up. Consider point closed. | All Steps | Open | Confirm procedure in place to use protable dehumidifiers in the short term until all upgrades are complete to allow for robust control iof humidity in CNC areas. | Production Equipment Dept. / Wenyi Zhang 生产设备部/张文艺 | QA / Meijia Liu QA/刘美佳
30 | BLA | Asymchem to provide vent header drawings and designs to Lilly for review. | Prior to Demo | Low < 1 week | 2026-09-28 | Has been provided. | -- | -- |  | All Steps | Completed |  | Engineering / Hongjie Guo IEPE / Guorui Zhang 工程/郭宏杰 IEPE/张国睿 | QA / Meijia Liu QA/刘美佳
31 | BLA/technical | Evaluate process-specific cross-contamination risks from process connections and utility lines, then develop a long-term plan to isolate nonessential connections or otherwise mitigate identified risks. Assess shared-utility and equipment-isolation requirements for GG917 and LAARA operations | Prior to Demo | Med > 1 week < 1 Month | 2026-10-04 | No detailed assessment in the CCS document. | Add a detailed assessment to the CCS document. | -- | Is there a general procedure/process in place that describes Asymchems approach to changeover and segregation practices? JOB: Lilly will review CCS and provide feedback | All Steps | Open |  | Production / Linchong Liu 生产/刘林冲 | QA / Qi Wang, Mingyang Yang QA/王琪，杨明旸
32 | BLA | Implement the use of permeable film to cover the ends of process and water hoses while stored for drying | Prior to Demo | Med > 1 week < 1 Month | 2026-10-04 | No permeable film is used to cover the ends of process and water hoses. | Use permeable film to cover the ends of process and water hoses. | -- | Confirm that permeable films are compatable with all process/solvent solutions. If not, and the process/solvent is non-growth promoting, use clean, solid cap instead. | All Steps | Open | Prevent hose contamination during Demo processing that could impact PPQ. | Production / Chunpeng Hu 生产/胡春鹏 | N/A
33 | BLA | Install low-point drains on the inlet and outlet of all PD pumps used in Category 4 systems, and add pre- and post-cleaning steps to drain from these points and nitrogen-purge through the pump to the outlet drain | Prior to Pre-PPQ | Med > 1 week < 1 Month | 2026-10-20 | This capability is already in place. | Prepare a checklist to include pre- and post-cleaning steps. | -- | AJM: Please confirm low-point drains on both sides of PD pumps are present. | Purification | Open |  | Production / Yanlong Li, Kai Liu 生产/李延龙，刘恺 | QA / Weijiang Liu QA/刘维江
34 | BLA | Update the cleaning program for PD pumps so recovery factors account for large-area soft parts and include a representative pump swab location for product-contact applications | Prior to Pre-PPQ | Med > 1 week < 1 Month | 2026-11-10 | The PD pump is rinse-sampled for residue testing. | Update the SOP to include swab sampling for residue testing. | -- | No additional follow up needed. | Purification | Open |  | Production / Kai Liu 生产/刘凯 | QA / Meijia Liu QA/刘美佳
35 | BLA | Evaluate long-term replacement of PD pumps with pressure transfer or hygienic centrifugal pumps with low-point casing drains; where PD pumps remain necessary, assess more drainable designs | Post PPQ | High > 1 month | 2027-01-30 | After use, both ends of the pump are drained and blown dry; a detailed operating procedure will be provided. | The corresponding hygienic centrifugal pumps are being procured. | -- | No additional follow up needed. | All Steps | Open |  | Engineering / Hongjie Guo Production / Junfeng Zhang 工程/郭宏杰 生产/张俊峰 | QA / Meijia Liu QA/刘美佳
36 | BLA | Several non-compliant items still exist against equipment/piping standards. For example, ball valves on Category 4 equipment/piping, for all steps long tank nozzles on vessel heads and/or branches off tank nozles that will not be cleanable during CIP, diptubes supported by hooks that form crevices, missing drains at low points (especially around filters), non-hygienic/cleanable instrument designs (level, temperature), flow meters installed in non-drainable, flanged connections on category 3 and 4 equipment/piping, bolted agitator blades, deadlegs in various locations due to use of non-zero-static valving/non-minimum distance tees, etc. Conduct a comprehensive gap assessment against equipment and piping standards and prioritize remediation of high-risk Category 3 and 4 systems before production start | Prior to Pre-PPQ | High > 1 month | Option 1: No CIP. Equipment connections meet 2D requirement; transfer piping section does not meet 3D requirement. Disassembly cleaning will be required afterwards. Completion date: 12/17/2026 Option 2: No CIP. Equipment connections meet 2D requirement with CIP ports reserved. Most of the transfer piping meets 2D requirement and minimum 3D requirement. Completion date: 01/20/2027 Option 3: In-line CIP. The vessel and piping are designed entirely following the 2D design philosophy. Completion date: 04/25/2027 | N/A | Redesign is in progress. Once the design is confirmed, the key items will be discussed with the Lilly team before execution. |  | AJM: Please explain what the Options in COlumn F mean in more details. Please share videos of progress when possible for Lilly to visually confirm acceptability. Also, where needed, please send design drawings for our confirmation before installing in field. I am most interested for how you are going to overcome the non-ideal instruments like the level transmitters and temperature elements as these are less straightforward to me than some of the other items. | All Steps | Open |  | Engineering / Hongjie Guo Production / Junfeng Zhang 工程/郭宏杰 生产/张俊峰 | QA / Mingzhi Chen QA/陈明志
37 | BLA | For equipment and piping gaps not remediated before production, establish direct traceability in cleaning documentation, including manual cleaning, targeted inspection, and cleaning or draining instructions for dead legs | Prior to Pre-PPQ | Med > 1 week < 1 Month | step1: 10/07/2026 step2: 10/20/2026 step3A: 11/09/2026 step3B: 11/28/2026 | -- | -- | -- | JOB: Update cleaning risk assessment | All Steps | Open |  | Production / Anyao Tang 生产/唐安垚 | QA / Weijiang Liu QA/刘维江
38 | BLA/technical | Purified Water header throughout the facility does not meet industry guidance - sample point is not representative of POU, no means of pre-use flushing/blowing, etc. Additionally, POU filtration should be provided for any PW supplied to a growth promoting solution via hose connection (upstream of drain line). These filters should have time in use tracked and be replaced frequently (NMT 24 hours). Implement point-of-use flushing directly to waste and post-use draining and drying for purified-water lines using zero-static valves or minimum-distance tees without creating dead legs 全厂纯化水（Purified Water） | Prior to Pre-PPQ | High > 1 month | Lead time: 6 weeks Modification: 3 weeks Passivation: 1 week Validation: 4 weeks 01/05/2027 | Temporary hoses are used to connect water outlets to the points of use. | -- | -- | Please clarify if there are similar gaps on Step 1/Step 2 for any process or cleaning water supply. Also, please update us on status of modifications via videos. Also, please confirm if we can have an interim solution in place while waiitng on zero-static valves (use of hoses/portable flow meters, use of just minimum distance tees/normal valves, etc.). Need to understand what our risk mitigations will be until long term modification can be in place. | All Steps | Open |  | Production / Chunpeng Hu Engineering / Hongjie Guo 生产/胡春鹏 工程/郭宏杰 | QA / Mingzhi Chen QA/陈明志
39 | BLA | Install point-of-use filters for purified water supplied by hose to growth-promoting solutions, track time in use, and replace filters no later than 24 hours | Prior to Pre-PPQ | Med > 1 week < 1 Month | 2026-10-20 | No requirement for filtration of purified water supplied by hose. | Add filtration and filter replacement-interval requirements to the MOR. | -- | AJM: Just to confirm, we only require these filters downstream of water hose connection if we are feeding a growth promoting solution. | Purification | Open |  | Production / Chunpeng Hu 生产/胡春鹏 | QA / Qi Wang QA/王琪
40 | BLA | Assess representative sampling from new point-of-use drains and determine whether formal revalidation or an informal verification study is required to confirm water-system quality | Prior to Pre-PPQ | High > 1 month | Lead time: 6 weeks Modification: 3 weeks Passivation: 1 week Validation: 4 weeks 01/05/2027 | Temporary hoses are used to connect water outlets to the points of use. | -- | Completing this before Pre-PPQ is tight. Could it be completed after PPQ, with water used per the current practice in the meantime? | AJM: See comment above. We will need to understand what the interim solution will look like and what data we can generate closer to client in the short term (abbreviated validation/ad hoc sampling protocol, etc.). | All Steps | Open |  | Production / Chunpeng Hu 生产/胡春鹏 | QA / Mingzhi Chen QA/陈明志
41 | BLA | Provide Lilly with the changeover strategy and governance for reused equipment, including cleaning limits, normally uncleaned lines, soft and hard-to-clean components, and replacement of filters, membranes, and resins | Prior to Pre-PPQ | Med > 1 week < 1 Month | 2026-10-30 | Equipment is disassembled for cleaning, and ARL performs Level 2 testing of the reflux solvent. The line from the activation tank to the synthesizer is reused after solvent flushing. | We will provide current practice to Lilly's team for discussion. | -- | AJM: Please advise when this will be provided for our review and comment. We want to make sure anything that is being re-used for our process (not new) is adequately changed over/cleaned/replaced - could you provide a list for each step clarifying what equipment has been previously used by a different process? | All Steps | Open |  | Production / Yanlong Li Fan Wang Linchong Liu 生产/李延龙 王帆 刘林冲 | QA / Zhiqiang Sun QA/孙志强
42 | BLA/technical | Define and document release controls for new equipment that demonstrate removal of fabrication and construction residues, debris and particulates, and acceptable bioburden before production use | Prior to Pre-PPQ | Med > 1 week < 1 Month | 2026-10-30 | -- | We will provide current practice to Lilly's team for discussion. | -- | AJM: Please advise when this will be provided for our review. | All Steps | Open |  | Production / Yanlong Li Kai Liu 生产/李延龙 刘恺 | QA / Zhiqiang Sun QA/孙志强
43 | BLA/technical | Execute spray coverage testing for all product-contact and growth-promoting equipment and incorporate qualified pressure, time, alarm limits, flow durations, and manual cleaning or swabbing of hard-to-clean areas into operating instructions | Prior to Pre-PPQ | Med > 1 week < 1 Month | Option 1: No CIP. Equipment connections meet 2D requirement; transfer piping section does not meet 3D requirement. Disassembly cleaning will be required afterwards. Completion date: 12/17/2026 Option 2: No CIP. Equipment connections meet 2D requirement with CIP ports reserved. Most of the transfer piping meets 2D requirement and minimum 3D requirement. Completion date: 01/20/2027 Option 3: In-line CIP. The vessel and piping are designed entirely following the 2D design philosophy. Completion date: 04/25/2027 | Spray coverage testing is performed on the equipment. | Spray coverage verification will be added after the modification is completed. | -- | AJM: Please ensure that results of spracy coverage are directly incorporated into cleaning records/SOPs (time, pressure, swab locations, etc.). | All Steps | Open |  | Production / Yanlong Li 生产/李延龙 | QA / Meijia Liu QA/刘美佳
44 | BLA | Determine and implement a means for visitors/support staff to wear a dedicated base layer in classified areas | Post PPQ | High > 1 month | 2026-12-10 | Asymchem has an internal gowning procedure for classified areas. The gowning procedure needs to be revisited. | Update the gowning procedure for classified areas. | -- | No additional follow up. | All Steps | Open | Follow up with Marie to understand acceptability. | Production / Kai Liu 生产/刘恺 | QA / Zhiqiang Sun QA/孙志强
45 | BLA | Provide Lilly with the operations access-control strategy and governance, including required training, approval criteria, and periodic roster review to remove or flag inappropriate access | Post PPQ | Med > 1 week < 1 Month | 2026-11-10 | Asymchem has an internal procedure for access control. Asymchem 已有门禁控制内部程序。 | Present the Asymchem access-control procedure to Lilly. 向 Lilly 介绍 Asymchem 门禁控制程序。 | -- | AJM: Please advise when procedure will be provided. | All Steps | Open |  | Production / Kai Liu 生产/刘恺 | QA / Meijia Liu QA/刘美佳
46 | BLA | Conduct hold-time studies for all portable vessels used for temporary water or growth-promoting solution storage, confirm complete drainability, and incorporate hold-time and draining requirements into operating documents. | Prior to Pre-PPQ | Med > 1 week < 1 Month | 2026-10-05 |  | This part of work has been completed. The documents will be presented to Lilly. | -- |  | All Steps | Completed | Limit refresh time to 48 hours, even if hold time is demonstrated to be longer. | R&D / Xinyi Zhu Production / Hui Ma 研发/朱新义 生产/马辉 | QA / Qi Wang QA/王琪
47 | Technical | Define controls that ensure only acceptable mobile phase is supplied to the process and specify the system response to out-of-range temperature, composition, or pH | Prior to Pre-PPQ | Low < 1 week | 2026-10-20 | Conductivity is monitored downstream of the solution-preparation mixer: acceptable mobile phase is routed to the mobile-phase tank, and out-of-range mobile phase is diverted to waste. Solution preparation is metered by mass flow meters, so temperature changes have little effect on the metered composition before mixing. pH probes are installed at the mixer and on the receiving mobile-phase tank for monitoring. | Please refer to the slides ( link in Column L) | -- | AJM: I will review provided information and revert back. | Purification | Open | Asymchem_Visit_Action_Tracker_Partial Feedback_09-29-2026.pptx | Production / Linchong Liu IEPE / Zhiheng Wang 生产/刘林冲 IEPE/王志恒 | QA / Meijia Liu QA/刘美佳
48 | BLA/technical | Provide the final pre-use and post-use filter integrity testing strategy | Prior to Pre-PPQ | Med > 1 week < 1 Month | 2026-10-20 | Asymchem has an internal procedure for filter integrity testing. | Present the Asymchem filter integrity testing strategy to Lilly. | -- | AJM: Please advise when strategy will be provided. | Purification | Open |  | Production / Yonggang Shi 生产/史永钢 | QA / Qi Wang QA/王琪
49 | Technical | Confirm AFD stroke height prevents blades from being submerged during displacement washes | Prior to Demo | Low < 1 week | 2026-09-30 | -- | Calculation shall be performed based on material volume and compared against the lifting height. Please refer to the slides ( link in Column L) | -- | AJM: I will review provided information and revert back. | Purification | Open | Asymchem_Visit_Action_Tracker_Partial Feedback_09-29-2026.pptx | Production / Yanlong Li 生产/李延龙 | N/A
50 | Technical | Define the mill operating strategy for final drug-substance sampling, inerting, target drum weight without overfill, screen-temperature monitoring, and operator ergonomics | Prior to Demo | Med > 1 week < 1 Month | 2026-09-27 | -- | Provide storyboard ppt | -- |  | Purification | Completed |  | Production / Yanlong Li 生产/李延龙 | N/A
51 | BLA/technical | Store hose ends at least 6 inches off the floor and provide a clear visual indicator confirming compliant storage position | Prior to Pre-PPQ | Med > 1 week < 1 Month | 2026-10-04 | No requirement for the height of purified water hose ends above the floor. | Update the SOP to add a minimum height requirement of 6 inches. | -- | AJM: Confirm visual indicator of 6 inches will be provided in field at sotrage locations (painted line, etc.). | Purification | Open |  | Production / Chunpeng Hu 生产/胡春鹏 | QA / Xiong Xiong QA/熊熊
52 | BLA/technical | Require contained devices for all solids-charging operations to prevent residual powder exposure to rooms and personnel. Require split valve charging strategy for all steps (including SPPS and cleavage). | Prior to Pre-PPQ | Med > 1 week < 1 Month | 2026-11-30 | -- | Purchased SBV, and will use SBV for all solids-charging operations |  | Based on timeline provided, does this mean we will plan to start PPQ without these present? JOB: Cleaning Documation updates will be necessary for SBV additions, MOR operation instructions updates, | All Steps | Open |  | Production / Yanlong Li 生产/李延龙 | N/A
53 | BLA | Walk down all lines containing diaphragm valves, verify correct installation angle for drainability, and correct noncompliant installations | Prior to Pre-PPQ | Med > 1 week < 1 Month | Option 1: No CIP. Equipment connections meet 2D requirement; transfer piping section does not meet 3D requirement. Disassembly cleaning will be required afterwards. Completion date: 12/17/2026 Option 2: No CIP. Equipment connections meet 2D requirement with CIP ports reserved. Most of the transfer piping meets 2D requirement and minimum 3D requirement. Completion date: 01/20/2027 Option 3: In-line CIP. The vessel and piping are designed entirely following the 2D design philosophy. Completion date: 04/25/2027 | -- | Redesign is in progress. Once the design is confirmed, the key items will be discussed with the Lilly team before execution. |  | AJM: Not following response here. This is just simple action to correct diaphragm valves already existing. | All Steps | Open |  | Engineering / Hongjie Guo 工程/郭宏杰 | QA / Mingzhi Chen QA/陈明志
54 | Technical | Ensure representative sampling capability exists for every required process sample while minimizing product loss | Prior to Pre-PPQ | Low < 1 week | 2026-10-25 | -- | Install a sampling valve on the 100 L preparation drums. | -- | AJM: Not following response. I would expect to see a sample map for the process (listing every sample to be pulled) and then confirmation that sampling capability exists - from where will you pull that sample (valve ID, location). | Purification | Open |  | Engineering / Hongjie Guo Production / Yanlong Li 工程/郭宏杰 生产/李延龙 | QA / Qi Wang QA/王琪
55 | BLA/technical | Update calibration instructions to keep tanks capped while non-retractable pH probes are calibrated, and evaluate replacement with retractable probe housings | Prior to Pre-PPQ | Med > 1 week < 1 Month | 2026-12-07 |  | Retractable pH purchased, install once arrival. Leadtime 8 weeks. |  | AJM: What will be interim solution for PPQ since this installation will have to occur after PPQ start? | Purification | Open |  | Production / Yanlong Li 生产/李延龙 | QA / Mingzhi Chen QA/陈明志

## Sheet1
Category | Implementation Timing | Implementation Effort | Scope
BLA | Prior to Pre-PPQ | Low < 1 week | All Steps
Technical | Prior to Demo | Med > 1 week < 1 Month | SPPS
BLA/technical | Post PPQ | High > 1 month | Cleavage
Impurity Investigation |  |  | Purification

## Summary
BLA Visit Action Tracker Summary BLA 来访行动项跟踪汇总
Metric 指标 | Count 数量 | Priority 优先级 | Count 数量
Total Actions 行动项总数 | 55 | High 高 | 9
High Priority 高优先级 | 9 | Medium 中 | 31
Open 未关闭 | 51 | Low 低 | 15
In Progress 进行中 | 0
Blocked 阻塞 | 0
Completed 已完成 | 4

## Instructions (hidden)
How to Use This Tracker 本跟踪表使用说明
• Assign a named owner in the Suggested Owner column, replacing the suggested function if appropriate. • 在建议负责人一栏指定具体责任人；如适用，替换建议的职能。
• Set a due date for every High-priority item. • 为每个高优先级事项设定截止日期。
• Use the Status dropdown to update progress. • 使用“状态”下拉列表更新进展。
• Use table filters to review actions by day, area, priority, owner, or status. • 使用表格筛选，按日期、区域、优先级、责任人或状态查看行动项。
• Priorities and owners are suggested organizational fields derived from the visit notes and should be confirmed by the project team. • 优先级与责任人为根据来访记录建议的组织字段，需由项目团队确认。